Operator’s Checklist

Visual Monthly Inspections

Underground Storage Tank Systems

RSA 146-C:19 and Env-Or 406.18 require monthly and annual visual inspections by or under the direction of the Class A or B operator at an Underground Storage Tank facility.

| Date of Inspection: UST Facility ID Number: Facility Name: Name of Class B operator directing the inspection: Name of person conducting inspection: Signature of person conducting the inspection: |
| --- |
| ( if true ; ( if false; Y to indicate corrective work was completed; N/A if not applicable |
| Tank # (See OneStop for correct tank numbers): |  |  |  |  |
| (1) Each vent riser shows no visible damage. |  |  |  |  |
| Repaired? |  |  |  |  |
| (2) Each pressure/vacuum vent cap and/or rain cap shows no visible damage. |  |  |  |  |
| Replaced? |  |  |  |  |
| (3) Each spill bucket shows no presence of oil, water, or debris. |  |  |  |  |
| Removed and disposed of content in accordance with all applicable federal, state, and local requirements? |  |  |  |  |
| (4) For double-walled spill buckets, including single-walled buckets installed within single-walled sumps, gauge indicates no oil or water, or electronic sensor is not in alarm. *Must be conducted for triennial tightness testing exemption, per Env-Or 406.12(e)* |  |  |  |  |
| Removed and disposed of content in accordance with all applicable federal, state, and local requirements? Repaired? |  |  |  |  |
| (5) Each fill adaptor cap, whether coaxial, two-point fill adaptor cap, and/or dry break adaptor cap is not loose, and shows presence of a gasket and tightness of fit. |  |  |  |  |
| Tightened, Repaired or Replaced? |  |  |  |  |
| (6) Each fill adaptor, whether coaxial, two-point fill adaptor, and/or dry break adaptor shows tightness of fit, |  |  |  |  |
| Tightened or replaced? |  |  |  |  |
| (7) Each fill pipe was free of any obstruction. |  |  |  |  |
| Obstruction Removed? |  |  |  |  |
| (8) Each dry break poppet valve shows a continuous seal, that depresses evenly across the valve seat, and reseats properly. |  |  |  |  |
| Repaired or replaced? |  |  |  |  |
| Tank #: |  |  |  |  |
| (9) Each motor fuel dispenser hose shows no tears, leaks, holes, kinks, crimps or defects of any kind. |  |  |  |  |
| Repaired or Replaced? |  |  |  |  |
| (10) Each motor fuel dispenser nozzle shows no leak or defects of any kind. |  |  |  |  |
| Repaired or Replaced? |  |  |  |  |
| (11) *Annually for All Dispenser Sumps and Cabinets* Each motor fuel dispenser cabinet interior and sump shows no evidence of leaking components and shows no oil, water, or debris present. Last date completed: _________________________ If checked annually, the last inspection of the dispenser cabinets was conducted on: ___________________________ |  |  |  |  |
| Repair and disposed of content in accordance with all applicable federal, state, and local requirements? |  |  |  |  |
| (12) Each oil transfer and dispensing area shows no presence of oil spills. |  |  |  |  |
| Reported and remediate any spill in accordance with all applicable federal, state, and local requirements? |  |  |  |  |
| (13) Each oil transfer and dispensing pad area shows no conditions such as open joints, cracking, spalling, nozzles extending beyond the pad, or other defects |  |  |  |  |
| Repaired or Replaced? |  |  |  |  |
| (14) Each leak, interstitial and product monitoring system enunciation panel is operating properly, including monitoring systems also associated with day tanks |  |  |  |  |
| Repaired or replaced? |  |  |  |  |
| (15) *Annually for All Containment Sumps* Each containment sump is free of leaking components and the presence of oil, water, or debris. Last date completed: __________________________ |  |  |  |  |
| Removed and disposed of content in accordance with all applicable federal, state, and local requirements? Repaired? |  |  |  |  |
| (16 *Annually for Double-Walled Sumps Only* Each interstitial space is free of any oil or water. Last date completed: ___________________ |  |  |  |  |
| Removed and disposed of content in accordance with all applicable federal, state, and local requirements? Repaired? |  |  |  |  |
| (17) *Annually for Double-Walled Sumps and Spill Buckets Only* Remove and inspect each sensor/gauge for proper length and functionality. Last date completed: __________________________ |  |  |  |  |
| Repaired or replaced? |  |  |  |  |

The certified operator shall document each monthly maintenance inspection, including all findings and repairs made.

Please keep this form with your records for a period of no less than 3 years.

Please attached any repair or maintenance notes to this monthly inspection form.